{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["Sheet1","data"],"not_rendered":{"charts":0,"images":77,"macros":1,"external_links":0,"defined_names":6,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":46,"n_cols":9,"rows_kept":46,"cut":false,"hidden":false,"merged":[[49,0,49,14],[33,2,33,3],[33,7,33,8],[33,9,33,10],[35,2,35,3],[35,4,35,11],[36,2,36,3],[36,7,36,8],[36,9,36,10],[38,2,38,3],[38,4,38,11],[39,2,39,3],[39,7,39,8],[45,3,47,9],[31,2,31,3],[31,7,31,8],[31,9,31,10],[32,2,32,3],[32,7,32,8],[32,9,32,10],[30,0,30,1],[30,2,30,3],[30,4,30,11],[15,2,15,3],[17,2,17,3],[19,2,19,5],[20,0,20,1],[20,2,20,3],[20,4,21,4],[20,5,21,5],[21,2,21,3],[23,1,23,13],[25,0,25,1],[26,6,26,11],[27,2,27,11],[28,2,28,11],[14,3,14,5],[5,3,5,5],[6,3,6,5],[8,0,8,1],[8,2,9,2],[8,3,8,5],[9,3,9,5],[10,3,10,5],[11,2,11,5],[12,0,12,1],[12,3,12,5],[13,3,13,5],[0,0,0,14],[1,0,1,1],[1,5,1,11],[2,1,2,13],[4,0,4,1],[4,3,4,5]]}
[]
[null,null,null,null,null,"Fibox Thermal Calculator\n\nVersion: X20 - Date: 27/6/2014"]
[null,"INPUT"]
[]
["1. Product selection",null,"Product family","ARCA"]
[null,null,"Size",{"$f":"data!$C$4","v":"ARCA 500x400x210"},null,null,null,null,{"$f":"AREA","v":0.66659999999999997}]
[null,null,"Direction","Vertical"]
[null,null,null,null,null,null,null,null,{"$f":"ROUNDDOWN(data!$E$2*data!$D$7*200,-1)","v":430}]
["2. Installation",null,"Installation","Pole mounting "]
[]
[null,null,"Inner door","None"]
[null,null,{"$f":"CONCATENATE(\"Empty Cabinet Max Power * = \",ROUND(data!$G$42,0),\" Watt\")","v":"Empty Cabinet Max Power * = 77 Watt"}]
["3. Environment",null,"Indoor / Outdoor","Indoor"]
[null,null,"Location","Europe"]
[null,null,"-Only when exposed \nto direct sunlight"]
[null,null,"Ambient temperature",null,35,"℃"]
[null,null,"Max. = 80℃\nMin. = -40℃\n",null,5,"℃"]
[null,null,"Cabinet temperature",null,70,"℃"]
[null,null,"Max. = 120℃\nMin. = -40℃",null,0,"℃"]
[null,null,{"$f":"CONCATENATE(\"Power from solar radiation (peak) = \",data!$O$42,\" Watt\")","v":"Power from solar radiation (peak) = - Watt"}]
["4. Components",null,"Power dissipation",null,0,"Watt"]
[null,null,{"$f":"CONCATENATE(\"Max. = \",$I$8,CHAR(10),\"Min. = 0\")","v":"Max. = 430\nMin. = 0"}]
[]
[null,"OUTPUT"]
[]
["Without cooling",null,"Estimated Ti max",35,"℃"]
[null,null,"Allowed Ti max",70,"℃",null,"77 Watt left to Estimated Pd max"]
[]
[null,null,"No External Cooling required."]
[]
["Recommendations",null,"Cooling solution",null,"Specification"]
[]
[]
[]
[]
[null,null,"Heating solution",null,"Specification"]
[]
[]
[null,null,"Condensation prevention",null,"Specification"]
[null,null,"Ventilation plug",null,null,null,null,"None"]
[]
[null,null,"Note & assumptions:","1. Heater's safety factor is 2"]
[null,null,null,"2. Air flow's safety factor is 1.25"]
[null,null,null,"3. Heat exchanger's safety factor is 1.25"]
[null,null,null,"4. Cabinet material PC's solar absorptance is 0.44"]
[null,null,null,"*5. According to IEC standards, the estimated Max Power is based on Ta max 35℃ and Ti max 70℃"]

{"sheet":"data","index":1,"n_rows":112,"n_cols":221,"rows_kept":112,"cut":false,"hidden":false,"merged":[[0,40,0,46],[0,47,0,109],[0,187,0,199],[0,200,0,205],[0,206,0,220],[5,6,5,12],[5,13,5,19],[0,110,0,133],[0,134,0,143],[0,144,0,153],[0,154,0,163],[0,164,0,171],[0,172,0,186],[0,6,0,12],[0,13,0,19],[0,20,0,27],[0,28,0,39]]}
["Size","Direction","Inner","Installation","Final K",null,"without inner door",null,null,null,null,null,null,"with inner door",null,null,null,null,null,null,"CAB PN",null,null,null,null,null,null,null,"CAB PX",null,null,null,null,null,null,null,null,null,null,null,"CAB P",null,null,null,null,null,null,"CAB SL",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"TBSL",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SLN",null,null,null,null,null,null,null,null,null,"ARCA JIG (US)",null,null,null,null,null,null,null,null,null,"CAB PC/ABS",null,null,null,null,null,null,null,null,null,"QUICK",null,null,null,null,null,null,null,"EK",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SOLID PC/ABS",null,null,null,null,null,null,null,null,null,null,null,null,"SM",null,null,null,null,null,"STCP/STC"]
[{"$f":"VLOOKUP($A$4,$B$60:$C$73,2,FALSE)","v":"500x400x210"},{"$f":"Sheet1!$D$7","v":"Vertical"},{"$f":"Sheet1!$D$11","v":"None"},{"$f":"LEN(Sheet1!$D$9)*10000+LEN(Sheet1!$D$7)*100+LEN($C$59)","v":140806},{"$f":"VLOOKUP($D$2,$A$7:$HM$34,IF($A$4=\"ARCA\",MATCH($C$4,$G$2:$M$2,0)+IF($C$2=\"Yes\",13,6),MATCH($C$4,$U$2:$HM$2,0)+20),FALSE)","v":3.3},null,"ARCA 300x200x150","ARCA 400x300x150","ARCA 400x300x210","ARCA 500x400x210","ARCA 600x400x210","ARCA 700x500x300","ARCA 800x600x300","ARCA 300x200x150","ARCA 400x300x150","ARCA 400x300x210","ARCA 500x400x210","ARCA 600x400x210","ARCA 700x500x300","ARCA 800x600x300","CAB PN 300x250x140","CAB PN 400x300x200","CAB PN 400x400x200","CAB PN 500x400x200","CAB PN 600x400x230","CAB PN 600x500x230","CAB PN 800x300x230","CAB PN 800x600x300","CAB PX 500x500x320","CAB PX 500x750x320","CAB PX 750x500x320","CAB PX 750x750x320","CAB PX 750x1000x320","CAB PX 750x1250x320","CAB PX 1000x500x320","CAB PX 1000x750x320","CAB PX 1000x1000x320","CAB PX 1000x1250x320","CAB PX 1250x750x320","CAB PX 1250x1000x320","CAB P 315x215x170","CAB P 415x315x170","CAB P 515x415x230","CAB P 615x415x230","CAB P 735x535x270","CAB P 835x635x300","CAB P 1035x835x300","CAB SL 300x200x150","CAB SL 200x300x150","CAB SL 300x300x150","CAB SL 300x300x210","CAB SL 300x300x250","CAB SL 400x300x150","CAB SL 400x300x210","CAB SL 400x300x250","CAB SL 500x300x210","CAB SL 300x400x150","CAB SL 300x400x210","CAB SL 300x400x250","CAB SL 400x400x150","CAB SL 400x400x210","CAB SL 400x400x250","CAB SL 400x400x300","CAB SL 500x400x210","CAB SL 500x400x250","CAB SL 500x400x300","CAB SL 600x400x210","CAB SL 600x400x250","CAB SL 600x400x300","CAB SL 800x400x210","CAB SL 800x400x250","CAB SL 800x400x300","CAB SL 1000x400x250","CAB SL 1000x400x300","CAB SL 500x500x210","CAB SL 500x500x300","CAB SL 600x500x210","CAB SL 600x500x250","CAB SL 600x500x300","CAB SL 700x500x250","CAB SL 400x600x210","CAB SL 400x600x250","CAB SL 400x600x300","CAB SL 500x600x300","CAB SL 600x600x210","CAB SL 600x600x250","CAB SL 600x600x300","CAB SL 600x600x400","CAB SL 800x600x210","CAB SL 800x600x250","CAB SL 800x600x300","CAB SL 800x600x400","CAB SL 1000x600x250","CAB SL 1000x600x300","CAB SL 1000x600x400","CAB SL 1200x600x250","CAB SL 1200x600x300","CAB SL 1200x600x400","CAB SL 600x800x250","CAB SL 600x800x300","CAB SL 800x800x210","CAB SL 800x800x250","CAB SL 800x800x300","CAB SL 800x800x400","CAB SL 1000x800x250","CAB SL 1000x800x300","CAB SL 1000x800x400","CAB SL 1200x800x250","CAB SL 1200x800x300","CAB SL 1200x800x400","TBSL 150x150x80","TBSL 150x200x80","TBSL 200x200x80","TBSL 250x200x80","TBSL 250x250x80","TBSL 300x250x80","TBSL 300x300x80","TBSL 300x400x80","TBSL 150x150x100","TBSL 150x200x100","TBSL 200x200x100","TBSL 250x200x100","TBSL 250x250x100","TBSL 300x250x100","TBSL 300x300x100","TBSL 300x400x100","TBSL 150x150x120","TBSL 150x200x120","TBSL 200x200x120","TBSL 250x200x120","TBSL 250x250x120","TBSL 300x250x120","TBSL 300x300x120","TBSL 300x400x120","SLN 320x220x180","SLN 320x220x260","SLN 320x320x180","SLN 320x320x260","SLN 440x320x180","SLN 440x320x260","SLN 640x320x180","SLN 640x320x260","SLN 640x440x180","SLN 640x440x260","ARCA JIG (US) 152x152x102","ARCA JIG (US) 203x152x127","ARCA JIG (US) 203x203x102","ARCA JIG (US) 254x203x102","ARCA JIG (US) 254x203x152","ARCA JIG (US) 254x254x152","ARCA JIG (US) 305x254x152","ARCA JIG (US) 356x305x178","ARCA JIG (US) 406x356x203","ARCA JIG (US) 457x406x254","CAB PC/ABS 150x150x110","CAB PC/ABS 250x150x110","CAB PC/ABS 350x250x150","CAB PC/ABS 300x200x180","CAB PC/ABS 300x300x180","CAB PC/ABS 400x300x180","CAB PC/ABS 400x300x160","CAB PC/ABS 450x350x160","CAB PC/ABS 500x400x200","CAB PC/ABS 600x400x220","QUICK 300x200x170","QUICK 300x300x170","QUICK 400x300x170","QUICK 400x300x230","QUICK 400x400x170","QUICK 600x300x170","QUICK 600x400x210","QUICK 600x400x270","EK 190x190x130","EK 190x190x180","EK 280x190x130","EK 280x190x180","EK 380x190x130","EK 380x190x180","EK 280x280x130","EK 280x280x180","EK 380x280x130","EK 380x280x180","EK 380x280x230","EK 560x280x130","EK 560x280x180","EK 560x380x180","EK 760x560x250","SOLID PC/ABS 188x188x130","SOLID PC/ABS 188x188x180","SOLID PC/ABS 278x188x130","SOLID PC/ABS 278x188x180","SOLID PC/ABS 378x188x130","SOLID PC/ABS 378x188x180","SOLID PC/ABS 278x278x130","SOLID PC/ABS 278x278x180","SOLID PC/ABS 378x278x130","SOLID PC/ABS 378x278x180","SOLID PC/ABS 558x278x130","SOLID PC/ABS 558x378x180","SOLID PC/ABS 757x559x250","SM 188x278x130","SM 188x278x180","SM 278x278x130","SM 278x278x180","SM 278x378x130","SM 278x378x180","STCP/STC 1275(420)x265x250","STCP/STC 1435(580)x265x250","STCP/STC 1695(840)x265x250","STCP/STC 1275(420)x400x250","STCP/STC 1435(580)x400x250","STCP/STC 1695(840)x400x250","STCP/STC 1730(880)x400x320","STCP/STC 1275(420)x530x250","STCP/STC 1435(580)x530x250","STCP/STC 1695(840)x530x250","STCP/STC 1730(880)x530x320","STCP/STC 1290(420)x660x250","STCP/STC 1420(580)x660x250","STCP/STC 1730(840)x660x250","STCP/STC 1730(880)x660x320"]
["Product",null,null,null,null,"H",300,400,400,500,600,700,800,300,400,400,500,600,700,800,300,400,400,500,600,600,800,800,500,500,750,750,750,750,1000,1000,1000,1000,1250,1250,315,415,515,615,735,835,1035,300,200,300,300,300,400,400,400,500,300,300,300,400,400,400,400,500,500,500,600,600,600,800,800,800,1000,1000,500,500,600,600,600,700,400,400,400,500,600,600,600,600,800,800,800,800,1000,1000,1000,1200,1200,1200,600,600,800,800,800,800,1000,1000,1000,1200,1200,1200,150,150,200,250,250,300,300,300,150,150,200,250,250,300,300,300,150,150,200,250,250,300,300,300,320,320,320,320,440,440,640,640,640,640,152,203,203,254,254,254,305,356,406,457,150,250,350,300,300,400,400,450,500,600,300,300,400,400,400,600,600,600,190,190,280,280,380,380,280,280,380,380,380,560,560,560,760,188,188,278,278,378,378,278,278,378,378,558,558,757,188,188,278,278,278,278,420,580,840,420,580,840,880,420,580,840,880,420,580,840,880]
[{"$f":"Sheet1!$D$5","v":"ARCA"},null,{"$f":"CONCATENATE(A4,\" \",A2)","v":"ARCA 500x400x210"},null,null,"W",200,300,300,400,400,500,600,200,300,300,400,400,500,600,250,300,400,400,400,500,300,600,500,750,500,750,1000,1250,500,750,1000,1250,750,1000,215,315,415,415,535,635,835,200,300,300,300,300,300,300,300,300,400,400,400,400,400,400,400,400,400,400,400,400,400,400,400,400,400,400,500,500,500,500,500,500,600,600,600,600,600,600,600,600,600,600,600,600,600,600,600,600,600,600,800,800,800,800,800,800,800,800,800,800,800,800,150,200,200,200,250,250,300,400,150,200,200,200,250,250,300,400,150,200,200,200,250,250,300,400,220,220,320,320,320,320,320,320,440,440,152,152,203,203,203,254,254,305,356,406,150,150,250,200,300,300,300,350,400,400,200,300,300,300,400,300,400,400,190,190,190,190,190,190,280,280,280,280,280,280,280,380,560,188,188,188,188,188,188,278,278,278,278,278,378,559,278,278,278,278,378,378,265,265,265,400,400,400,400,530,530,530,530,660,660,660,660]
[null,null,null,null,null,"D",150,150,210,210,210,300,300,150,150,210,210,210,300,300,140,200,200,200,230,230,230,300,320,320,320,320,320,320,320,320,320,320,320,320,170,170,230,230,270,300,300,150,150,150,210,250,150,210,250,210,150,210,250,150,210,250,300,210,250,300,210,250,300,210,250,300,250,300,210,300,210,250,300,250,210,250,300,300,210,250,300,400,210,250,300,400,250,300,400,250,300,400,250,300,210,250,300,400,250,300,400,250,300,400,80,80,80,80,80,80,80,80,100,100,100,100,100,100,100,100,120,120,120,120,120,120,120,120,180,260,180,260,180,260,180,260,180,260,102,127,102,102,152,152,152,178,203,254,110,110,150,180,180,180,160,160,200,220,170,170,170,230,170,170,210,270,130,180,130,180,130,180,130,180,130,180,230,130,180,180,250,130,180,130,180,130,180,130,180,130,180,130,180,250,130,180,130,180,130,180,250,250,250,250,250,250,320,250,250,250,320,250,250,250,320]
[null,"Installation","Picture","Effective area","Top area",null,"K value without inner door",null,null,null,null,null,null,"K value with inner door"]
[140806,"Single",null,{"$f":"(1.8*H*(W+D)+1.4*W*D)/1000000","v":0.66659999999999997},{"$f":"W*D/1000000","v":8.4000000000000005E-2},null,3.1,3.1,3.1,3.3,3.3,3.3,3.3,2.7,2.7,2.7,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.7,3.5,3.6,3.6,3.6,3.7,3.6,3.7,3.5,3.8,3.6,3.6,3.7,3.6,3.6,3.6,3.4,3.7,3.5,3.6,3.6,3.6,3.6,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.3,3.3,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[140810,"End of Row",null,{"$f":"(1.8*H*W+1.4*D*(H+W))/1000000","v":0.62460000000000004},{"$f":"W*D/1000000","v":8.4000000000000005E-2},null,3.1,3.1,3.1,3.3,3.3,3.3,3.3,2.7,2.7,2.7,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.7,3.5,3.6,3.6,3.6,3.7,3.6,3.7,3.5,3.8,3.6,3.6,3.7,3.6,3.6,3.6,3.4,3.7,3.5,3.6,3.6,3.6,3.6,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.7,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.7,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[140813,"Intermediated",null,{"$f":"(1.8*H*W+H*D+1.4*W*D)/1000000","v":0.58260000000000001},{"$f":"W*D/1000000","v":8.4000000000000005E-2},null,3.1,3.1,3.1,3.3,3.3,3.3,3.3,2.7,2.7,2.7,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.7,3.5,3.6,3.6,3.6,3.7,3.6,3.7,3.5,3.8,3.6,3.6,3.7,3.6,3.6,3.6,3.4,3.7,3.5,3.6,3.6,3.6,3.6,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.3,3.3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.7,3.7,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.7,3.7,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[140811,"Top covered",null,{"$f":"(1.8*H*(W+D)+0.7*W*D)/1000000","v":0.60780000000000001},{"$f":"W*D/1000000*0.15","v":1.26E-2},null,2.9,2.9,2.9,3.3,3.3,3.3,3.3,2.4,2.4,2.4,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.3,3.9,3.4,3.7,3.8,3.6,3.8,3.6,4,3.6,3.8,3.7,3.7,3.6,3.7,3.8,3.7,3.7,3.8,3.9,3.7,3.7,3.8,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,3.3,3.3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[140814,"Bottom covered",null,{"$f":"(1.8*H*(W+D)+1.4*W*D)/1000000","v":0.66659999999999997},{"$f":"W*D/1000000","v":8.4000000000000005E-2},null,3.1,3.1,3.1,3.3,3.3,3.3,3.3,2.7,2.7,2.7,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.7,3.5,3.6,3.6,3.6,3.7,3.6,3.7,3.5,3.8,3.6,3.6,3.7,3.6,3.6,3.6,3.4,3.7,3.5,3.6,3.6,3.6,3.6,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.3,3.3,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[140820,"Top & Bottom covered",null,{"$f":"(1.8*H*(W+D)+0.7*W*D)/1000000","v":0.60780000000000001},{"$f":"W*D/1000000*0.15","v":1.26E-2},null,2.9,2.9,2.9,3.3,3.3,3.3,3.3,2.4,2.4,2.4,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.3,3.9,3.4,3.7,3.8,3.6,3.8,3.6,4,3.6,3.8,3.7,3.7,3.6,3.7,3.8,3.7,3.7,3.8,3.9,3.7,3.7,3.8,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,3.3,3.3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[140812," Surrounded ",null,{"$f":"(H*D+1.8*H*W+0.7*W*D)/1000000","v":0.52380000000000004},{"$f":"W*D/1000000*0.1","v":8.4000000000000012E-3},null,2.9,2.9,2.9,3.3,3.3,3.3,3.3,2.4,2.4,2.4,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.3,3.9,3.4,3.7,3.8,3.6,3.8,3.6,4,3.6,3.8,3.7,3.7,3.6,3.7,3.8,3.7,3.7,3.8,3.9,3.7,3.7,3.8,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,3.3,3.3,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.5,3.5,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.5,3.5,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[130806,null,null,{"$f":"(1.8*H*D+1.4*W*(H+D))/1000000","v":0.58660000000000001},{"$f":"W*D/1000000","v":8.4000000000000005E-2},null,3.1,3.1,3.1,3.3,3.3,3.3,3.3,2.7,2.7,2.7,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.7,4,3.7,3.8,3.6,3.7,3.7,3.8,3.6,3.8,3.8,3.6,3.8,3.7,3.6,3.7,3.8,3.7,3.7,3.8,3.6,3.6,3.7,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.3,3.3,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[130810,null,null,{"$f":"(1.4*H*(W+D)+1.4*W*D)/1000000","v":0.54459999999999997},{"$f":"W*D/1000000","v":8.4000000000000005E-2},null,3.1,3.1,3.1,3.3,3.3,3.3,3.3,2.7,2.7,2.7,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.9,3.5,3.7,3.8,3.6,3.8,3.7,3.7,3.5,3.8,3.6,3.7,3.8,3.6,3.7,3.8,3.5,3.7,3.7,3.7,3.7,3.8,3.8,3.8,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.3,3.3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.7,3.7,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.7,3.7,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[130813,null,null,{"$f":"(H*D+1.4*W*(H+D))/1000000","v":0.50260000000000005},{"$f":"W*D/1000000","v":8.4000000000000005E-2},null,3.1,3.1,3.1,3.3,3.3,3.3,3.3,2.7,2.7,2.7,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.8,3.7,3.6,3.6,3.8,3.8,3.6,3.7,3.8,4,3.6,3.7,3.7,3.7,3.8,3.6,3.4,3.7,3.5,3.6,3.8,3.6,3.6,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.3,3.3,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.6,3.6,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.6,3.6,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[130811,null,null,{"$f":"(1.8*H*D+1.4*H*W+0.7*W*D)/1000000","v":0.52780000000000005},{"$f":"W*D/1000000*0.15","v":1.26E-2},null,2.9,2.9,2.9,3.3,3.3,3.3,3.3,2.4,2.4,2.4,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.3,3.9,3.4,3.7,3.8,3.6,3.8,3.6,4,3.6,3.8,3.7,3.7,3.6,3.7,3.8,3.7,3.7,3.8,3.9,3.7,3.7,3.8,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,3.3,3.3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[130814,null,null,{"$f":"(1.8*H*D+1.4*W*(H+D))/1000000","v":0.58660000000000001},{"$f":"W*D/1000000","v":8.4000000000000005E-2},null,3.1,3.1,3.1,3.3,3.3,3.3,3.3,2.7,2.7,2.7,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.7,3.5,3.6,3.6,3.6,3.7,3.6,3.7,3.5,3.8,3.6,3.6,3.7,3.6,3.6,3.6,3.4,3.7,3.5,3.6,3.6,3.6,3.6,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.3,3.3,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[130820,null,null,{"$f":"(1.8*H*D+1.4*H*W+0.7*W*D)/1000000","v":0.52780000000000005},{"$f":"W*D/1000000*0.15","v":1.26E-2},null,2.9,2.9,2.9,3.3,3.3,3.3,3.3,2.4,2.4,2.4,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.3,3.9,3.4,3.7,3.8,3.6,3.8,3.6,4,3.6,3.8,3.7,3.7,3.6,3.7,3.8,3.7,3.7,3.8,3.9,3.7,3.7,3.8,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,3.3,3.3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[130812,null,null,{"$f":"(0.7*W*D+H*D+1.4*H*W)/1000000","v":0.44379999999999997},{"$f":"W*D/1000000*0.1","v":8.4000000000000012E-3},null,2.9,2.9,2.9,3.3,3.3,3.3,3.3,2.4,2.4,2.4,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.3,3.9,3.4,3.7,3.8,3.6,3.8,3.6,4,3.6,3.8,3.7,3.7,3.6,3.7,3.8,3.7,3.7,3.8,3.9,3.7,3.7,3.8,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,3.3,3.3,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.5,3.5,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.5,3.5,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[141006,null,null,{"$f":"(1.8*W*(H+D)+1.4*H*D)/1000000","v":0.65820000000000001},{"$f":"H*D/1000000","v":0.105},null,3.3,3.3,3.3,3.5,3.5,3.5,3.5,2.9,2.9,2.9,3.2,3.2,3.2,3.2,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.7,3.5,3.6,3.6,3.6,3.7,3.6,3.7,3.5,3.8,3.6,3.6,3.7,3.6,3.6,3.6,3.4,3.7,3.5,3.6,3.6,3.6,3.6,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.5,3.5,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[141010,null,null,{"$f":"(1.8*H*W+1.4*D*(H+W))/1000000","v":0.62460000000000004},{"$f":"H*D/1000000","v":0.105},null,3.3,3.3,3.3,3.5,3.5,3.5,3.5,2.9,2.9,2.9,3.2,3.2,3.2,3.2,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.7,3.5,3.6,3.6,3.6,3.7,3.6,3.7,3.5,3.8,3.6,3.6,3.7,3.6,3.6,3.6,3.4,3.7,3.5,3.6,3.6,3.6,3.6,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.5,3.5,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.7,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.7,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[141013,null,null,{"$f":"(1.8*H*W+W*D+1.4*H*D)/1000000","v":0.59099999999999997},{"$f":"H*D/1000000","v":0.105},null,3.3,3.3,3.3,3.5,3.5,3.5,3.5,2.9,2.9,2.9,3.2,3.2,3.2,3.2,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.7,3.5,3.6,3.6,3.6,3.7,3.6,3.7,3.5,3.8,3.6,3.6,3.7,3.6,3.6,3.6,3.4,3.7,3.5,3.6,3.6,3.6,3.6,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.5,3.5,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.7,3.7,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.7,3.7,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[141011,null,null,{"$f":"(1.8*W*(H+D)+0.7*H*D)/1000000","v":0.5847},{"$f":"H*D/1000000*0.15","v":1.575E-2},null,3.1,3.1,3.1,3.3,3.3,3.3,3.3,2.7,2.7,2.7,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.3,3.9,3.4,3.7,3.8,3.6,3.8,3.6,4,3.6,3.8,3.7,3.7,3.6,3.7,3.8,3.7,3.7,3.8,3.9,3.7,3.7,3.8,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.3,3.3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[141014,null,null,{"$f":"(1.8*W*(H+D)+1.4*H*D)/1000000","v":0.65820000000000001},{"$f":"H*D/1000000","v":0.105},null,3.3,3.3,3.3,3.5,3.5,3.5,3.5,2.9,2.9,2.9,3.2,3.2,3.2,3.2,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.7,3.5,3.6,3.6,3.6,3.7,3.6,3.7,3.5,3.8,3.6,3.6,3.7,3.6,3.6,3.6,3.4,3.7,3.5,3.6,3.6,3.6,3.6,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.5,3.5,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[141020,null,null,{"$f":"(1.8*W*(H+D)+0.7*H*D)/1000000","v":0.5847},{"$f":"H*D/1000000*0.15","v":1.575E-2},null,3.1,3.1,3.1,3.3,3.3,3.3,3.3,2.7,2.7,2.7,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.3,3.9,3.4,3.7,3.8,3.6,3.8,3.6,4,3.6,3.8,3.7,3.7,3.6,3.7,3.8,3.7,3.7,3.8,3.9,3.7,3.7,3.8,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.3,3.3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[141012,null,null,{"$f":"(W*D+1.8*H*W+0.7*H*D)/1000000","v":0.51749999999999996},{"$f":"H*D/1000000*0.1","v":1.0500000000000001E-2},null,3.1,3.1,3.1,3.3,3.3,3.3,3.3,2.7,2.7,2.7,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.3,3.9,3.4,3.7,3.8,3.6,3.8,3.6,4,3.6,3.8,3.7,3.7,3.6,3.7,3.8,3.7,3.7,3.8,3.9,3.7,3.7,3.8,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.3,3.3,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.5,3.5,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.5,3.5,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[131006,null,null,{"$f":"(1.8*W*D+1.4*H*(W+D))/1000000","v":0.57820000000000005},{"$f":"H*D/1000000","v":0.105},null,3.3,3.3,3.3,3.5,3.5,3.5,3.5,2.9,2.9,2.9,3.2,3.2,3.2,3.2,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.7,4,3.7,3.8,3.6,3.7,3.7,3.8,3.6,3.8,3.8,3.6,3.8,3.7,3.6,3.7,3.8,3.7,3.7,3.8,3.6,3.6,3.7,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.5,3.5,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[131010,null,null,{"$f":"(1.4*W*(H+D)+1.4*H*D)/1000000","v":0.54459999999999997},{"$f":"H*D/1000000","v":0.105},null,3.3,3.3,3.3,3.5,3.5,3.5,3.5,2.9,2.9,2.9,3.2,3.2,3.2,3.2,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.9,3.5,3.7,3.8,3.6,3.8,3.7,3.7,3.5,3.8,3.6,3.7,3.8,3.6,3.7,3.8,3.5,3.7,3.7,3.7,3.7,3.8,3.8,3.8,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.5,3.5,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.7,3.7,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.7,3.7,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[131013,null,null,{"$f":"(W*D+1.4*H*(W+D))/1000000","v":0.51100000000000001},{"$f":"H*D/1000000","v":0.105},null,3.3,3.3,3.3,3.5,3.5,3.5,3.5,2.9,2.9,2.9,3.2,3.2,3.2,3.2,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.8,3.7,3.6,3.6,3.8,3.8,3.6,3.7,3.8,4,3.6,3.7,3.7,3.7,3.8,3.6,3.4,3.7,3.5,3.6,3.8,3.6,3.6,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.6,3.6,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.6,3.6,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[131011,null,null,{"$f":"(1.8*W*D+1.4*H*W+0.7*H*D)/1000000","v":0.50470000000000004},{"$f":"H*D/1000000*0.15","v":1.575E-2},null,3.1,3.1,3.1,3.3,3.3,3.3,3.3,2.7,2.7,2.7,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.3,3.9,3.4,3.7,3.8,3.6,3.8,3.6,4,3.6,3.8,3.7,3.7,3.6,3.7,3.8,3.7,3.7,3.8,3.9,3.7,3.7,3.8,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.3,3.3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[131014,null,null,{"$f":"(1.8*W*D+1.4*H*(W+D))/1000000","v":0.57820000000000005},{"$f":"H*D/1000000","v":0.105},null,3.3,3.3,3.3,3.5,3.5,3.5,3.5,2.9,2.9,2.9,3.2,3.2,3.2,3.2,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.7,3.5,3.6,3.6,3.6,3.7,3.6,3.7,3.5,3.8,3.6,3.6,3.7,3.6,3.6,3.6,3.4,3.7,3.5,3.6,3.6,3.6,3.6,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.5,3.5,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.7,3.7,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[131020,null,null,{"$f":"(1.8*W*D+1.4*H*W+0.7*H*D)/1000000","v":0.50470000000000004},{"$f":"H*D/1000000*0.15","v":1.575E-2},null,3.1,3.1,3.1,3.3,3.3,3.3,3.3,2.7,2.7,2.7,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.9,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.3,3.9,3.4,3.7,3.8,3.6,3.8,3.6,4,3.6,3.8,3.7,3.7,3.6,3.7,3.8,3.7,3.7,3.8,3.9,3.7,3.7,3.8,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.3,3.3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3.4,3.4,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[131012,null,null,{"$f":"(0.7*H*D+W*D+1.4*H*W)/1000000","v":0.4375},{"$f":"H*D/1000000*0.1","v":1.0500000000000001E-2},null,3.1,3.1,3.1,3.3,3.3,3.3,3.3,2.7,2.7,2.7,3,3,3,3,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.4,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,2.7,2.7,2.7,2.7,2.7,3.1,3.1,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.6,3.3,3.9,3.4,3.7,3.8,3.6,3.8,3.6,4,3.6,3.8,3.7,3.7,3.6,3.7,3.8,3.7,3.7,3.8,3.9,3.7,3.7,3.8,3.7,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.1,3.3,3.3,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.5,3.5,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.5,3.5,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.2,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3,3.3]
[]
[]
[]
[null,{"$f":"Sheet1!$D$13","v":"Indoor"}]
["Indoor",null,null,null,null,null,null,null,{"$f":"IF(Sheet1!$D$14=\"Asia\",0,1)","v":1}]
["Outdoor"]
["Direct Sunlight",null,null,null,null,null,"Max power",null,"city","Latitude","Latitude","Peak","Absorption","Final radiation"]
[null,null,null,null,null,null,{"$f":"Sheet1!$I$6*$E$2*35","v":76.992299999999986},null,{"$f":"VLOOKUP(Sheet1!$D$14,$A$45:$B$49,2,FALSE)","v":"Helsinki"},{"$f":"VLOOKUP($I$42,INDIRECT(ADDRESS(50,MATCH(Sheet1!$D$14,$G$48:$O$48,0)+6)&\":\"&ADDRESS(107,MATCH(Sheet1!$D$14,$G$48:$O$48,0)+7)),2,FALSE)","v":"50° ~ 66.5°"},"0° ~ 23.5°",967.41669999999999,0.44,{"$f":"VLOOKUP($J$42,$K$42:$L$46,2)*$M$42*VLOOKUP($D$2,$A$7:$E$34,5,FALSE)","v":29.448859440000003},{"$f":"IF($B$38=\"Direct Sunlight\",ROUND($N$42,0),\"-\")","v":"-"}]
[null,null,null,null,null,null,null,null,null,null,"23.5° ~ 40°",959.00699999999995]
[null,null,null,null,null,null,null,null,null,null,"40° ~ 50°",899.75210000000004]
["Africa","Abuja",null,null,null,null,null,null,null,null,"50° ~ 66.5°",796.77650000000006]
["Americas","Asuncion",null,null,null,null,null,null,null,null,"66.5° ~ 90°",601.65970000000004]
["Asia","Taipei"]
["Europe","Helsinki",null,null,null,null,"Asia",null,"Europe",null,"Africa",null,"Oceania",null,"Americas"]
["Oceania","Apia",null,null,null,null,"city","latitude","city","latitude","city","latitude","city","latitude","city","latitude",null,null,"ARCA","CAB PX","CAB P","EK","CAB PN","CAB SL","TBSL","SLN","ARCA JIG (US)","CAB PC/ABS","QUICK","SOLID PC/ABS","SM","STCP/STC"]
[null,"Single","Single","Single","Single",null,"Abu Dhabi ","23.5° ~ 40°","Aalborg","50° ~ 66.5°","Abuja","0° ~ 23.5°","Apia","0° ~ 23.5°","Asuncion","23.5° ~ 40°",null,"ARCA","300x200x150","500x500x320","315x215x170","190x190x130","300x250x140","300x200x150","150x150x80","320x220x180","152x152x102","150x150x110","300x200x170","188x188x130","188x278x130","1275(420)x265x250"]
["Wall mounting","Single","Single","Single","Single",null,"Amman","23.5° ~ 40°","Aarhus","50° ~ 66.5°","Accra","0° ~ 23.5°","Canberra","23.5° ~ 40°","Basseterre","0° ~ 23.5°",null,"CAB PN","400x300x150","500x750x320","415x315x170","190x190x180","400x300x200","200x300x150","150x200x80","320x220x260","203x152x127","250x150x110","300x300x170","188x188x180","188x278x180","1435(580)x265x250"]
["Pole mounting ","End of Row","End of Row","Intermediated",null,null,"Ankara","23.5° ~ 40°","Aberdeen","50° ~ 66.5°","Addis Ababa ","0° ~ 23.5°","Funafuti","0° ~ 23.5°","Belmopan","0° ~ 23.5°",null,"CAB SL","400x300x210","750x500x320","515x415x230","280x190x130","400x400x200","300x300x150","200x200x80","320x320x180","203x203x102","350x250x150","400x300x170","278x188x130","278x278x130","1695(840)x265x250"]
[null,"Intermediated","Intermediated"," Surrounded ",null,null,"Ashgabat","23.5° ~ 40°","Amsterdam","50° ~ 66.5°","Algiers","23.5° ~ 40°","Honiara","0° ~ 23.5°","Bogotá","0° ~ 23.5°",null,"CAB P","500x400x210","750x750x320","615x415x230","280x190x180","500x400x200","300x300x210","250x200x80","320x320x260","254x203x102","300x200x180","400x300x230","278x188x180","278x278x180","1275(420)x400x250"]
["Vertical"," Surrounded ","Top covered",null,null,null,"Astana","50° ~ 66.5°","Andorra la Vella","40° ~ 50°","Antananarivo","0° ~ 23.5°","Koror","0° ~ 23.5°","Brasília","0° ~ 23.5°",null,"CAB PX","600x400x210","750x1000x320","735x535x270","380x190x130","600x400x230","300x300x250","250x250x80","440x320x180","254x203x152","300x300x180","400x400x170","378x188x130","278x378x130","1435(580)x400x250"]
["Horizontal",null,"Bottom covered",null,null,null,"Baghdad","23.5° ~ 40°","Athens","23.5° ~ 40°","Asmara","0° ~ 23.5°","Majuro","0° ~ 23.5°","Bridgetown","0° ~ 23.5°",null,"EK","700x500x300","750x1250x320","835x635x300","380x190x180","600x500x230","400x300x150","300x250x80","440x320x260","254x254x152","400x300x180","600x300x170","378x188x180","278x378x180","1695(840)x400x250"]
[null,null,"Top & Bottom covered",null,null,null,"Baku","23.5° ~ 40°","Bamako","0° ~ 23.5°","Bamako","0° ~ 23.5°","Nukuʻalofa","0° ~ 23.5°","Buenos Aires ","23.5° ~ 40°",null,"TBSL","800x600x300","1000x500x320","1035x835x300","280x280x130","800x300x230","400x300x210","300x300x80","640x320x180","305x254x152","400x300x160","600x400x210","278x278x130",null,"1730(880)x400x320"]
["None",null," Surrounded ",null,null,null,"Bandar Seri Begawan ","0° ~ 23.5°","Berlin","50° ~ 66.5°","Bangui","0° ~ 23.5°","Palikir","0° ~ 23.5°","Caracas","0° ~ 23.5°",null,null,null,"1000x750x320",null,"280x280x180","800x600x300","400x300x250","300x400x80","640x320x260","356x305x178","450x350x160","600x400x270","278x278x180",null,"1275(420)x530x250"]
["Yes",null,null,null,null,null,"Bangkok","0° ~ 23.5°","Bern","40° ~ 50°","Banjul","0° ~ 23.5°","Port Moresby ","0° ~ 23.5°","Castries","0° ~ 23.5°",null,null,null,"1000x1000x320",null,"380x280x130",null,"500x300x210","150x150x100","640x440x180","406x356x203","500x400x200",null,"378x278x130",null,"1435(580)x530x250"]
[null,null,{"$f":"VLOOKUP($A$4,$B$60:$D$73,3)","v":"Single"},null,null,null,"Beijing","23.5° ~ 40°","Bratislava","40° ~ 50°","Bissau","0° ~ 23.5°","Port Vila","0° ~ 23.5°","Chicago","40° ~ 50°",null,null,null,"1000x1250x320",null,"380x280x180",null,"300x400x150","150x200x100","640x440x260","457x406x254","600x400x220",null,"378x278x180",null,"1695(840)x530x250"]
[null,"ARCA","500x400x210",{"$f":"$C$50","v":"Single"},null,null,"Beirut","23.5° ~ 40°","Brussels","40° ~ 50°","Brazzaville","0° ~ 23.5°","Suva","0° ~ 23.5°","Dallas","23.5° ~ 40°",null,null,null,"1250x750x320",null,"380x280x230",null,"300x400x210","200x200x100",null,null,null,null,"558x278x130",null,"1730(880)x530x320"]
[null,"CAB PN","300x250x140","Single",null,null,"Bishkek","40° ~ 50°","Bucharest","40° ~ 50°","Bujumbura","0° ~ 23.5°","Tarawa","0° ~ 23.5°","Georgetown","0° ~ 23.5°",null,null,null,"1250x1000x320",null,"560x280x130",null,"300x400x250","250x200x100",null,null,null,null,"558x378x180",null,"1290(420)x660x250"]
[null,"CAB SL","300x200x150","Single",null,null,"Chongqing","23.5° ~ 40°","Budapest","40° ~ 50°","Cairo","23.5° ~ 40°","Wellington","40° ~ 50°","Guatemala","0° ~ 23.5°",null,null,null,null,null,"560x280x180",null,"400x400x150","250x250x100",null,null,null,null,"757x559x250",null,"1420(580)x660x250"]
[null,"CAB P","315x215x170","Single",null,null,"Colombo","0° ~ 23.5°","Chișinău","40° ~ 50°","Cape Town","23.5° ~ 40°","Yaren District ","0° ~ 23.5°","Havana","23.5° ~ 40°",null,null,null,null,null,"560x380x180",null,"400x400x210","300x250x100",null,null,null,null,null,null,"1730(840)x660x250"]
[null,"CAB PX","500x500x320","Single",null,null,"Damascus","23.5° ~ 40°","Copenhagen","50° ~ 66.5°","Conakry","0° ~ 23.5°",null,null,"Houston","23.5° ~ 40°",null,null,null,null,null,"760x560x250",null,"400x400x250","300x300x100",null,null,null,null,null,null,"1730(880)x660x320"]
[null,"EK","190x190x130","Single",null,null,"Dhaka","0° ~ 23.5°","Dublin","50° ~ 66.5°","Dakar","0° ~ 23.5°",null,null,"Kingston","0° ~ 23.5°",null,null,null,null,null,null,null,"400x400x300","300x400x100"]
[null,"TBSL","150x150x80",{"$f":"$C$50","v":"Single"},null,null,"Dili","0° ~ 23.5°","Edinburgh","50° ~ 66.5°","Djibouti","0° ~ 23.5°",null,null,"Kingstown","0° ~ 23.5°",null,null,null,null,null,null,null,"500x400x210","150x150x120"]
[null,"SLN","320x220x180",{"$f":"$C$50","v":"Single"},null,null,"Doha","23.5° ~ 40°","Glasgow","50° ~ 66.5°","Dodoma","0° ~ 23.5°",null,null,"Lima","0° ~ 23.5°",null,null,null,null,null,null,null,"500x400x250","150x200x120"]
[null,"ARCA JIG (US)","203x203x102",{"$f":"$C$50","v":"Single"},null,null,"Dushanbe","23.5° ~ 40°","Hamburg","50° ~ 66.5°","Freetown","0° ~ 23.5°",null,null,"Managua","0° ~ 23.5°",null,null,null,null,null,null,null,"500x400x300","200x200x120"]
[null,"CAB PC/ABS","150x150x110","Single",null,null,"Guangzhou","0° ~ 23.5°","Helsinki","50° ~ 66.5°","Gaborone","23.5° ~ 40°",null,null,"Mexico City ","0° ~ 23.5°",null,null,null,null,null,null,null,"600x400x210","250x200x120"]
[null,"QUICK","600x400x210","Single",null,null,"Hanoi","0° ~ 23.5°","Kiev","40° ~ 50°","Harare","0° ~ 23.5°",null,null,"Montevide","23.5° ~ 40°",null,null,null,null,null,null,null,"600x400x250","250x250x120"]
[null,"SOLID PC/ABS","188x188x130","Single",null,null,"Islamabad","23.5° ~ 40°","Kiruna","66.5° ~ 90°","Johannesburg","23.5° ~ 40°",null,null,"Nassau","23.5° ~ 40°",null,null,null,null,null,null,null,"600x400x300","300x250x120"]
[null,"SM","188x278x130","Single",null,null,"Jakarta","0° ~ 23.5°","Lisbon","23.5° ~ 40°","Kampala","0° ~ 23.5°",null,null,"New York City","40° ~ 50°",null,null,null,null,null,null,null,"800x400x210","300x300x120"]
[null,"STCP/STC","1275(420)x265x250",{"$f":"$C$50","v":"Single"},null,null,"Jerusalem","23.5° ~ 40°","Ljubljana","40° ~ 50°","Khartoum","0° ~ 23.5°",null,null,"Ottawa","40° ~ 50°",null,null,null,null,null,null,null,"800x400x250","300x400x120"]
[null,null,null,null,null,null,"Kabul","23.5° ~ 40°","London","50° ~ 66.5°","Kigali","0° ~ 23.5°",null,null,"Panama City","0° ~ 23.5°",null,null,null,null,null,null,null,"800x400x300"]
[null,null,null,null,null,null,"Kaohsiung","0° ~ 23.5°","Luxembourg","40° ~ 50°","Kinshasa","0° ~ 23.5°",null,null,"Paramaribo","0° ~ 23.5°",null,null,null,null,null,null,null,"1000x400x250"]
[null,null,null,null,null,null,"Kathmandu","23.5° ~ 40°","Madrid","23.5° ~ 40°","Libreville","0° ~ 23.5°",null,null,"Port of Spain ","0° ~ 23.5°",null,null,null,null,null,null,null,"1000x400x300"]
[null,null,null,null,null,null,"Kolkata","0° ~ 23.5°","Malmö","50° ~ 66.5°","Lilongwe","0° ~ 23.5°",null,null,"Port-au-Prince ","0° ~ 23.5°",null,null,null,null,null,null,null,"500x500x210"]
[null,null,null,null,null,null,"Kuala Lumpur ","0° ~ 23.5°","Marseille","40° ~ 50°","Lome","0° ~ 23.5°",null,null,"Quito","0° ~ 23.5°",null,null,null,null,null,null,null,"500x500x300"]
[null,null,null,null,null,null,"Kuwait","23.5° ~ 40°","Milan","40° ~ 50°","Luanda","0° ~ 23.5°",null,null,"Roseau","0° ~ 23.5°",null,null,null,null,null,null,null,"600x500x210"]
[null,null,null,null,null,null,"Malé","0° ~ 23.5°","Minsk","50° ~ 66.5°","Lusaka","0° ~ 23.5°",null,null,"San Jose ","23.5° ~ 40°",null,null,null,null,null,null,null,"600x500x250"]
[null,null,null,null,null,null,"Manama","23.5° ~ 40°","Monaco","40° ~ 50°","Malabo","0° ~ 23.5°",null,null,"San Salvador ","0° ~ 23.5°",null,null,null,null,null,null,null,"600x500x300"]
[null,null,null,null,null,null,"Manila","0° ~ 23.5°","Moscow","50° ~ 66.5°","Maputo","23.5° ~ 40°",null,null,"Santiago","23.5° ~ 40°",null,null,null,null,null,null,null,"700x500x250"]
[null,null,null,null,null,null,"Mumbai","0° ~ 23.5°","Munich","40° ~ 50°","Maseru","23.5° ~ 40°",null,null,"Santo Domingo","0° ~ 23.5°",null,null,null,null,null,null,null,"400x600x210"]
[null,null,null,null,null,null,"Muscat","0° ~ 23.5°","Novosibirsk","50° ~ 66.5°","Mbabane","23.5° ~ 40°",null,null,"St. George's","0° ~ 23.5°",null,null,null,null,null,null,null,"400x600x250"]
[null,null,null,null,null,null,"New Delhi","23.5° ~ 40°","Oslo","50° ~ 66.5°","Mogadishu","0° ~ 23.5°",null,null,"St. John's","40° ~ 50°",null,null,null,null,null,null,null,"400x600x300"]
[null,null,null,null,null,null,"Nicosia","23.5° ~ 40°","Paris","40° ~ 50°","Monrovia","0° ~ 23.5°",null,null,"Sucre","0° ~ 23.5°",null,null,null,null,null,null,null,"500x600x300"]
[null,null,null,null,null,null,"Osaka","23.5° ~ 40°","Prague ","40° ~ 50°","Moroni, Comoros","0° ~ 23.5°",null,null,"Tegucigalpa","0° ~ 23.5°",null,null,null,null,null,null,null,"600x600x210"]
[null,null,null,null,null,null,"Phnom Penh ","0° ~ 23.5°","Reykjavík","50° ~ 66.5°","Nairobi","0° ~ 23.5°",null,null,"Washington","23.5° ~ 40°",null,null,null,null,null,null,null,"600x600x250"]
[null,null,null,null,null,null,"Pyongyang","23.5° ~ 40°","Riga","50° ~ 66.5°","N'Djamena","0° ~ 23.5°",null,null,null,null,null,null,null,null,null,null,null,"600x600x300"]
[null,null,null,null,null,null,"Riyadh","23.5° ~ 40°","Rome","40° ~ 50°","Niamey","0° ~ 23.5°",null,null,null,null,null,null,null,null,null,null,null,"600x600x400"]
[null,null,null,null,null,null,"Sana'a","0° ~ 23.5°","Rovaniemi","50° ~ 66.5°","Nouakchott","0° ~ 23.5°",null,null,null,null,null,null,null,null,null,null,null,"800x600x210"]
[null,null,null,null,null,null,"Sapporo","40° ~ 50°","Saint Petersburg","50° ~ 66.5°","Ouagadougou","0° ~ 23.5°",null,null,null,null,null,null,null,null,null,null,null,"800x600x250"]
[null,null,null,null,null,null,"Seoul","23.5° ~ 40°","San Marino","40° ~ 50°","Port Louis ","0° ~ 23.5°",null,null,null,null,null,null,null,null,null,null,null,"800x600x300"]
[null,null,null,null,null,null,"Shanghai","23.5° ~ 40°","Sarajevo","40° ~ 50°","Porto Novo","0° ~ 23.5°",null,null,null,null,null,null,null,null,null,null,null,"800x600x400"]
[null,null,null,null,null,null,"Singapore","0° ~ 23.5°","Skopje","40° ~ 50°","Praia","0° ~ 23.5°",null,null,null,null,null,null,null,null,null,null,null,"1000x600x250"]
[null,null,null,null,null,null,"Taichung","23.5° ~ 40°","Sofia","40° ~ 50°","Rabat","23.5° ~ 40°",null,null,null,null,null,null,null,null,null,null,null,"1000x600x300"]
[null,null,null,null,null,null,"Taipei","0° ~ 23.5°","Stockholm","50° ~ 66.5°","São Tomé","0° ~ 23.5°",null,null,null,null,null,null,null,null,null,null,null,"1000x600x400"]
[null,null,null,null,null,null,"Tashkent","40° ~ 50°","Tallinn","50° ~ 66.5°","Tripoli","23.5° ~ 40°",null,null,null,null,null,null,null,null,null,null,null,"1200x600x250"]
[null,null,null,null,null,null,"Tbilisi","40° ~ 50°","Tirana","40° ~ 50°","Tunis","23.5° ~ 40°",null,null,null,null,null,null,null,null,null,null,null,"1200x600x300"]
[null,null,null,null,null,null,"Tehran","23.5° ~ 40°","Umeå","50° ~ 66.5°","Victoria","0° ~ 23.5°",null,null,null,null,null,null,null,null,null,null,null,"1200x600x400"]
[null,null,null,null,null,null,"Thimphu","23.5° ~ 40°","Vaduz","40° ~ 50°","Windhoek","0° ~ 23.5°",null,null,null,null,null,null,null,null,null,null,null,"600x800x250"]
[null,null,null,null,null,null,"Tokyo","23.5° ~ 40°","Vatican City","40° ~ 50°","Yamoussoukro","0° ~ 23.5°",null,null,null,null,null,null,null,null,null,null,null,"600x800x300"]
[null,null,null,null,null,null,"Vientiane","0° ~ 23.5°","Vienna","40° ~ 50°","Yaoundé","0° ~ 23.5°",null,null,null,null,null,null,null,null,null,null,null,"800x800x210"]
[null,null,null,null,null,null,"Yangon","0° ~ 23.5°","Vilnius","50° ~ 66.5°",null,null,null,null,null,null,null,null,null,null,null,null,null,"800x800x250"]
[null,null,null,null,null,null,"Yerevan","23.5° ~ 40°","Warsaw","50° ~ 66.5°",null,null,null,null,null,null,null,null,null,null,null,null,null,"800x800x300"]
[null,null,null,null,null,null,"Yokohama","23.5° ~ 40°","Yekaterinburg","50° ~ 66.5°",null,null,null,null,null,null,null,null,null,null,null,null,null,"800x800x400"]
[null,null,null,null,null,null,null,null,"Zagreb","40° ~ 50°",null,null,null,null,null,null,null,null,null,null,null,null,null,"1000x800x250"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"1000x800x300"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"1000x800x400"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"1200x800x250"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"1200x800x300"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"1200x800x400"]